SECTION 6: BLOWDOWN SYSTEM SOP

Purpose: To safely reduce sediment accumulation and maintain boiler water quality by periodically discharging water from the boiler, bottom blowdown, and surface blowdown systems.

Procedures:

Confirm blowdown tank is empty and vented.

Verify water level is within safe limits before initiating blowdown. Open blowdown valve slowly to avoid thermal shock. Observe pressure drop and maintain for 10–20 seconds. Close valve gradually to prevent hammering.

Log time, pressure, and temperature during blowdown. Inspect valve integrity and piping after blowdown.

Notes:

Bottom blowdown should be performed daily or as specified. Surface blowdown frequency depends on conductivity and TDS testing.

Never perform blowdown with low water levels.