# Nexum Suum Training Module

Thermodynamics & Boiler Maintenance – Modules 3 & 4

Prepared by Nexum Suum Incorporated – Efficiency | Ethics | Leadership | Compliance

# Module 3 – Importance of Pressure, Precision & Temperature

## 3.1 Pressure

Definition: Pressure is the force exerted by steam or water per unit area, measured in psi or bar.
Role in Boilers: Defines whether steam is saturated, superheated, or at risk of flash boiling.
Ranges: Low-pressure boilers <15 psi steam, <160 psi water; High-pressure boilers >15 psi steam up to 1000+ psi.
Why It Matters: Too low = poor output. Too high = hazard. Governed by ASME Boiler & Pressure Vessel Code.
Complexity: Safety valves must relieve before MAWP. Calibration is legally required.

## 3.2 Temperature

Definition: Temperature measures the intensity of heat energy.
Ranges: Hot water boilers ~180–212°F. Steam boilers 300–1200°F depending on pressure.
Superheating: Raises steam temp above saturation, useful in turbines.
Why It Matters: Too low = condensation and corrosion. Too high = material stress, safety cutouts.

## 3.3 Precision & Calibration

Gauges: Pressure gauges, thermometers, and flow meters must be calibrated.
Calibration Methods:
• Pressure – deadweight tester, manometers.
• Temperature – ice point, boiling point, RTD calibration.
• Flow – calibrated orifice plates, ultrasonic meters.
Importance: An inaccurate gauge may display safe conditions while failure is imminent.
Complexity: Calibration mandated by OSHA/ASME/insurers on quarterly to annual basis.

# Module 4 – Calculations & Performance

## 4.1 Boiler Efficiency Equations

• Combustion Efficiency: Ratio of heat absorbed vs released, measured with O₂/CO₂/CO readings.
• Thermal Efficiency: (BTUs transferred ÷ BTUs input).
• Seasonal Efficiency: Accounts for start/stop and standby losses.

## 4.2 Steam Generation Calculations

Formula: lb steam/hr = (BTU input/hr × efficiency) ÷ enthalpy of steam.
Example: 10,000,000 BTU/hr × 0.80 ÷ 1150 ≈ 6,950 lb steam/hr.

## 4.3 Water-Side Calculations

• Formula: BTU/hr = GPM × ΔT × 500.
• NPSH (Net Positive Suction Head): Prevents pump cavitation.
Importance: Insufficient flow = hot spots, tube failures.

## 4.4 Fuel Calculations

Conversions:
• Natural Gas: 1 therm = 100,000 BTU. 1 CCF ≈ 102,000 BTU.
• Oil: #2 fuel oil ≈ 140,000 BTU/gal.
• Electricity: 1 kWh = 3,412 BTU.
Why It Matters: Savings calculated directly from these conversions.

## 4.5 Performance Monitoring

Indicators:
• Stack temperature.
• O₂/CO₂ readings.
• Feedwater temp.
• Blowdown rates.

Trending: Daily logging shows drift in performance before failures.
Complexity: Requires BMS integration or disciplined manual logging.