# NEXUM SUUM INC. — BOILER SYSTEMS SOP

Operational Excellence Through Efficiency and Compliance
(Diagram Edition – A4 Digital Format)

# Purpose & Scope

This SOP provides standardized operating, safety, and optimization guidance for all boiler system types: firetube, watertube, heat recovery, steam generators, and hot water units. It applies to stationary engineers, maintenance personnel, and facility operators who manage daily operations, tune-ups, and shutdowns under Nexum Suum compliance standards.

# Step-by-Step Procedure

## Pre-Start Inspection

- Inspect the boiler exterior for leaks, damage, or missing insulation.

- Verify LWCO (Low Water Cut-Off) operation — blow down and confirm water level return.

- Check fuel supply valves, regulators, and strainers for blockage or leaks.

- Inspect burner linkage, air damper, and flame safeguard control.

- Confirm stack damper is open and unobstructed.

- Review last calibration logs (combustion analyzer, pressure gauge).

## Startup Sequence

- Remove LOTO (Lockout/Tagout) devices and confirm authorization.

- Open main steam valve slightly to vent air from header.

- Start feedwater pump; confirm pressure and return flow.

- Engage burner on low fire, monitoring ignition stability via sight port.

- Gradually increase firing rate to reach desired steam pressure or temperature.

- Check sight glass for consistent water level and verify gauge alignment.

## Normal Operation

- Record stack temperature, O₂, and CO₂ readings every shift.

- Maintain O₂ between 3–5% for natural gas and 4–6% for oil.

- Ensure feedwater pump cycling is ≤6 starts/hour.

- Check condensate return temperature (target 190–210 °F).

- Perform bottom blowdown once per 8-hour shift (minimum).

- Test safety valve lift quarterly.

- Maintain DA tank pressure around 5–8 psig and vent open to atmosphere.

## Shutdown Procedure

- Reduce firing rate to low fire.

- Close fuel valve and maintain purge cycle for 60 seconds minimum.

- Close main steam stop valve and vent drum slowly.

- Drain when water temp <140 °F; tag unit 'offline – cooling.'

- Inspect burner, clean electrodes, and brush tubes if soot >1/32 inch.

- Log shutdown reason, date/time, and operator initials.

# Equations & Reference Formulas

| Metric | Formula | Example |
| --- | --- | --- |
| Boiler HP (BHP) | (Flow × PSI) ÷ (1714 × Eff) | (200 × 60) ÷ (1714 × 0.85) = 8.2 BHP |
| Steam Flow (lbs/hr) | BHP × 34.5 | 8.2 × 34.5 = 283 lbs/hr |
| Efficiency (%) | (Output BTU / Input BTU) × 100 | (900,000 / 1,000,000) × 100 = 90% |
| Fuel Cost ($) | CCF × Rate | 120 × 1.05 = $126/day |
| Condensate Recovery (%) | (Return Flow / Feed Flow) × 100 | (85 / 100) × 100 = 85% |

# Common Fault Examples

| Fault | Symptom | Cause | Corrective Action |
| --- | --- | --- | --- |
| Low Steam Pressure | Burner cycling | Fouled tubes or low feed temp | Brush tubes, adjust DA heater |
| Wet Steam / Water Hammer | Condensate carryover | High water level / LWCO dirty | Skim boiler surface blowdown |
| Stack Temp >450°F | Low efficiency | Excess air or soot | Clean tubes, reset O₂ trim |
| Flame Failure | No ignition | Flame rod dirty / gas pressure low | Clean sensor, verify regulator |
| Blowdown Water Cloudy | Poor treatment | Scale or contamination | Sample water, adjust chemicals |

# Optimization Guidance

- Perform monthly combustion tuning (record pre/post results in Sheets).

- Keep stack temp <100°F above steam temp for optimal efficiency.

- Maintain feedwater hardness ≤ 0.2 grains/gal.

- Use variable frequency drives (VFD) on pumps and blowers.

- Implement auto blowdown controller tied to conductivity probe.

- Use Google Sheets Boiler Log (CTS2) to track ΔT, runtime, and fuel cost trends.

# Regulatory References

- OSHA 1910.169: Pressure vessels and air receivers.

- ASME CSD-1: Controls & Safety Devices for Automatically Fired Boilers.

- EPA 40 CFR 63 Subpart JJJJJJ: Industrial/commercial boiler MACT compliance.

- NFPA 85: Boiler and Combustion Systems Hazards Code.

- NJAC 7:27-19.16: Annual Combustion Adjustment (New Jersey).