# 25NSBLC – Boiler Systems Daily Walkthrough & SOP Manual

# Daily Boiler Inspection – What to Look For

• Low Water Cutoff (LWCO) test response

• Normal Operating Water Level (NOWL) in sight glass

• Clean, clear sight glass

• Water column blowdown flow

• Stack temperature trends

• Burner flame color and stability

• Unusual burner noise or pulsing

• Combustion air fan sound

• Visible leaks (water, steam, fuel)

• Safety valve condition (no crusting, leaking)

• Pressure gauge reading vs setpoint

• Steam temperature and pressure trends

• Boiler shell and pipe insulation intact

• Burner cycling frequency

• Make-up water usage changes

• Feedwater pump operation

• Expansion tank pressure (hydronic)

• Flue gas smell or discoloration

• Operating log consistency vs previous day

• Control panel alarms or faults

# Boiler Daily Inspection Checklist

This checklist ensures efficiency by identifying any defects that could interrupt workflow.

| Task | Status | Trending/Notes |
| --- | --- | --- |
| Check flame through sight glass (clear, stable) | □ Pass □ Flag |  |
| Verify emergency shutoff is unobstructed | □ Pass □ Flag |  |
| Confirm area around boiler is dry, clean, clear of combustibles | □ Pass □ Flag |  |
| Inspect for visible leaks (fuel, water, steam) | □ None □ Detected |  |
| Check safety valves (tags + no obstruction) | □ Pass □ Flag |  |
| Flue Gas Reading (if available) | ___ ppm |  |
| Sound Level | □ Normal □ Unusual (describe) |  |
| Vibration on Fan Blower | □ Low □ Moderate □ Excessive |  |

# Boiler Interlock Safety Systems

These safety interlocks and shutdown protocols ensure safe operating practices and prevent equipment damage or personal injury.

| Interlock | Purpose | Efficiency Impact | Maintenance Tip |
| --- | --- | --- | --- |
| Low Water Cutoff (LWCO) | Shuts off burner if water level is too low | Prevents dry-firing, extending life | Test weekly |
| High Limit Aquastat | Cuts off burner at max temp | Prevents overheating & scale buildup | Verify settings quarterly |
| Flame Safeguard System | Monitors flame integrity & startup | Ensures clean ignition; reduces restarts | Test sensors & relays monthly |
| Pressuretrol/Modulating Controller | Controls firing rate based on pressure | Maintains steady loads, prevents short cycling | Calibrate annually |
| Flow Switch | Verifies water or steam flow | Prevents overheating from pump or flow failures | Inspect paddle or probe quarterly |
| Stack Temperature Sensor | Shuts burner if temp exceeds limit | Avoids wasted fuel from poor heat transfer | Log trends if available |
| E-Stop Safety Switch | Emergency system shutdown | Protects all systems and staff | Ensure accessibility & test monthly |

# Tips for Expanding Boiler Life

✅ 1. Implement Strict Water Treatment Protocols

Prevent scaling & corrosion with regular blowdowns and chemical feed monitoring. Use deaerators or oxygen scavengers. Log TDS and pH levels daily.

✅ 2. Perform Regular Blowdowns

Bottom blowdown removes sediment daily. Surface blowdown controls TDS. Use automated controls for consistency.

✅ 3. Cycle Boilers Intelligently

Avoid short-cycling. Use load-following strategies and fine-tune setpoints.

✅ 4. Maintain Combustion Efficiency

Schedule quarterly tuning. Check O₂, CO₂, and flue temps. Clean nozzles and ignition assemblies.

✅ 5. Insulate & Inspect

Ensure all hot piping and boiler shell are insulated. Inspect gaskets, doors, and seals for heat loss.

# Start-Up and Shutdown Procedures

## High-Temperature Hydronic Boiler Start-Up

1. Check isolation valves and air vents.

2. Power on control panel and verify safeties.

3. Open bypass loop valve to warm return water.

4. Engage circulation pumps.

5. Raise setpoint temperature slowly.

6. Verify expansion tank pressure matches temp.

7. Monitor outlet vs. return temp (≤ 40°F diff).

8. Log flue temp, water temp, and pressure.

💡 Tip: Never fire a hydronic boiler without proper flow.

## Steam Boiler Start-Up

1. Check water level (mid-sight glass).

2. Ensure valves are in correct position.

3. Warm feedwater.

4. Power on burner controls and purge air (~30 sec).

5. Light pilot, then main burner.

6. Bring boiler to pressure at ~25% firing rate.

7. Crack open steam header valve at ~80% line pressure.

8. Test LWCO and safety valves.

⚠️ Never bypass flame failure or LWCO safeties.

# Boiler Water Chemistry Instructions

Always follow proper PPE, SDS guidance, and use clean sample containers.

1. Alkalinity (OH) Test

Add 20 drops Barium Chloride + 2 drops Phenolphthalein to 25mL cooled sample. If pink, titrate with HCl until colorless. Record drops and multiply by factor.

2. Alkalinity (P & M) Test

Add 3 drops pH indicator to sample, titrate to clear (P-Alk). Add 3 drops Methyl Orange, titrate to orange (M-Alk). Total = M-Alk.

3. Hardness (Trace Test)

Add 5 drops buffer and 1 scoop indicator to sample. If red, titrate to blue. Multiply drops by 5 for ppm.

4. Sulfite Test

Add 1 drop pH indicator to cooled sample, titrate with sulfite titrant until colorless. Multiply drops by 5 for ppm.

# Boiler System Types and Manufacturer SOPs

## Shift-Wise 24-Hour SOP Tasks

### Morning (6 AM–2 PM)

• Log boiler pressure, steam output, and stack temp

• Inspect burner flame via sight port

• Check water level (sight glass or sensors)

• Verify LWCO, high limit, flame scanner

• Ensure blowdown is scheduled

• Check for leaks on valves and traps

• Calibrate O₂ sensor or note deviation

### Afternoon (2 PM–10 PM)

• Verify control panel vs. gauges

• Clean air filters (Aerco, Cleaver-Brooks)

• Record flue gas analyzer data

• Test emergency shutdown

• Inspect chemical injection and pump

• Check economizer temps (if present)

### Night (10 PM–6 AM)

• Cycle auto-blowdown

• Check feedwater temp and deaerator

• Inspect combustion air damper

• Review runtime and backup readiness

• Ensure lag boilers are prepped

• Flashlight check for carbon or hot spots

# Boiler Compliance Codes & Regulatory Requirements

Boiler systems must adhere to strict regulatory standards for materials, safety, emissions, and documentation. Non-compliance can lead to shutdowns, fines, and serious safety hazards. Below is a summary of key codes and their focus areas:

## 1. Certification & Authorization

✅ ASME Stamp (U, S, H) required for all pressure vessels

⚠️ Unauthorized fabrication or repair is illegal

✅ National Board R Stamp required for pressure-retaining repairs

✅ Licensed Operators (e.g., Red Seal, BOE) required for high-pressure systems

## 2. Material Testing & Traceability

✅ Traceable Mill Test Reports (MTRs) required

⚠️ NDT (RT, UT, PT, MT) testing required before commissioning

✅ Hydrostatic testing at 1.5× MAWP before startup

## 3. Combustion & Burner Safety

✅ NFPA 85 and CSD-1 require purge, flame safeguard, and interlocks

⚠️ Manual overrides or bypassing flame scanners are violations

## 4. Installation & Piping

✅ Must meet ASME Section I or VIII + NBIC Part 1

✅ Relief valves must be set and sized to MAWP

## 5. Safety Devices & Shutdown Controls

✅ Pressure relief valves tested annually and tagged

⚠️ Operating without active LWCO or high-limit = immediate shutdown

## 6. Documentation & Records

✅ Daily logs required for temp, pressure, flame

✅ WPS, PQR, WPQ must be available for inspection

## 7. Environmental & Regulatory

✅ Follow OSHA 1910 and EPA Clean Air Act thresholds

✅ SDS for all chemicals must be posted and accessible

⚠️ Illegal to discharge chemicals into storm drains

# Client Acknowledgment – Thank You

To our valued client,

Thank you for choosing Nexum Suum as your partner in boiler performance, safety, and optimization. Your investment in proactive maintenance, operational excellence, and compliance reflects true leadership.

Each checklist completed, valve inspected, and SOP followed helps you:
• Improve safety and reliability
• Maximize fuel efficiency and lower costs
• Align with ASME, NFPA, NBIC, and OSHA codes

We're honored to support your commitment to smarter, safer facilities.

Stay optimized. Stay ahead.

— The Nexum Suum Team
📧 razzellv@nexumsuum.com | 🌐 www.nexumsuum.com