# NEXUM SUUM INC. — CHILLER SYSTEMS SOP

Operational Excellence Through Efficiency and Compliance
(A4 Digital Format – All Chiller Types Included)

# Purpose & Scope

This SOP provides detailed instructions for startup, operation, shutdown, and maintenance of centrifugal, screw, scroll, absorption, air-cooled, and water-cooled chillers. It ensures safe, compliant, and efficient operation under Nexum Suum standards, incorporating OSHA, ASME, and EPA best practices.

# Step-by-Step Procedure

## Pre-Start Inspection

- Inspect oil level, refrigerant sight glass, and piping insulation integrity.

- Check condenser and evaporator water pumps for readiness.

- Verify chilled and condenser water flow through differential pressure gauges.

- Confirm cooling tower fans operational (for water-cooled units).

- Check compressor oil heater status (should be ON for ≥8 hrs before start).

- Ensure control panel power ON and no active alarms.

## Startup Procedure

- Open condenser and chilled water valves fully.

- Start condenser water pump; verify flow and pressure differential.

- Start chilled water pump; monitor pressure and ΔT across evaporator.

- Engage chiller in manual low-load mode (if available).

- Monitor suction, discharge, and oil pressures.

- Record entering/leaving water temperatures for condenser and evaporator.

## Normal Operation

- Monitor compressor amps; compare to rated full load amps (FLA).

- Maintain chilled water supply temp within ±1°F of setpoint.

- Check condenser approach (Temp Condenser Out – Ambient Wet Bulb ≤ 10°F).

- Observe refrigerant level; sight glass should be clear with minimal bubbles.

- Record pressures: Suction, Discharge, and Oil every 4 hours.

- Ensure VFDs (if installed) ramp smoothly without overcurrent faults.

## Shutdown Procedure

- Gradually reduce load to 30% before stopping chiller.

- Shut off compressor; allow post-lube pump to run for 5 minutes.

- Stop chilled water and condenser pumps after system equalizes.

- Close service valves and isolate unit for maintenance if needed.

- Log all operating data and shutdown reason in Sheets/CTS Log.

- Tag out system and perform oil/refrigerant sample if shutdown >30 days.

# Equations & Reference Formulas

| Metric | Formula | Example |
| --- | --- | --- |
| Tons of Refrigeration | (GPM × ΔT × 500) ÷ 12,000 | (480 × 10 × 500) ÷ 12,000 = 200 Tons |
| Coefficient of Performance (COP) | (Cooling kW Output / Input kW) | 703 / 200 = 3.52 |
| kW/Ton | Input kW / Tons | 200 / 200 = 1.0 kW/Ton |
| Approach Temp | Condenser Out Temp – Ambient Wet Bulb | 95 – 85 = 10°F |
| Evaporator ΔT | Return Temp – Supply Temp | 56 – 44 = 12°F |

# Common Fault Examples

| Fault | Symptom | Cause | Corrective Action |
| --- | --- | --- | --- |
| High Condenser Pressure | Condenser fan or pump fault | Dirty tubes or high ambient temp | Clean tubes, check flow and tower operation |
| Low Evaporator Pressure | Chilled water freeze risk | Low load or faulty TXV/EXV | Adjust control valve, verify refrigerant level |
| Oil High Temp | Lubrication degradation | Low oil level or high discharge temp | Top off oil, check oil cooler water flow |
| Compressor Trips on Overload | Excess amps | Faulty contactor or improper phase balance | Inspect wiring and motor windings |
| Air in System | Reduced cooling capacity | Improper purge or leak | Use purge unit and perform leak check |

# Optimization Guidance

- Clean condenser tubes every 1,000 hrs or quarterly, whichever comes first.

- Maintain condenser approach ≤10°F for optimal performance.

- Monitor ΔT daily; deviations >3°F indicate fouling or flow issues.

- Calibrate sensors and transmitters semi-annually.

- Verify proper refrigerant charge — excessive charge increases kW/Ton.

- Integrate Make.com + AWS QuickSight to visualize chiller performance metrics in real-time.

- Perform 'air burp' via vent valve at high point of condenser loop after refill to prevent air binding.

- Log daily suction/discharge pressure and OAT in CTS Log (for regression analysis).

# Regulatory & Compliance References

- ASHRAE 15: Safety Standard for Refrigeration Systems.

- ASHRAE 34: Designation and Safety Classification of Refrigerants.

- OSHA 1910.101: Compressed gases (anhydrous ammonia handling).

- EPA Section 608: Refrigerant recovery, recycling, and technician certification.

- NFPA 70: National Electrical Code for motor circuits and VFDs.

- ASME Section VIII: Pressure Vessels (for condenser shells).