# Nexum Suum Water Treatment & Chemistry SOP

## Purpose & Scope

This SOP establishes standardized procedures for the operation, monitoring, and maintenance of all water treatment systems within a facility—covering make-up, feedwater, condensate, cooling, and domestic systems. It ensures that water quality meets or exceeds regulatory, equipment, and safety standards by controlling scale, corrosion, and microbiological growth.

This applies to:
- Boiler feedwater systems (DA tanks, surge tanks, expansion tanks)
- Cooling towers and chiller condenser loops
- Domestic hot water and process water
- Reverse Osmosis (RO), Deionized (DI), and Water for Injection (WFI) systems
- Condensate recovery and return systems

## Flow Diagram (Simplified Process Overview)

CITY / WELL WATER
       ↓
  Softener / Filtration
       ↓
  Chemical Treatment (Dechlorination, pH control, anti-scalant)
       ↓
  Reverse Osmosis (RO)
       ↓
  Deaerator (for boiler feedwater)
       ↓
  Storage / Distribution Tanks
       ↓
  Heat Exchanger / Boiler / Chiller System
       ↓
  Return Lines → Condensate Recovery → DA Tank
       ↓
  Blowdown / Discharge → Neutralization → Drain

## Step-by-Step Procedures

### Startup Procedure

Pre-Inspection: Verify all valves, chemical feed tanks, sensors, and equipment are in normal operating position and leak-free.

System Fill & Circulation: Begin filling and circulating water through softeners and filters; record initial pressure, flow rate, and temperature.

Chemical Dosing: Start feed pumps to maintain boiler pH 8.5–10.5, sulfite >30 ppm, phosphate 20–40 ppm; cooling tower pH 7.5–9.0; conductivity ≤2,500 µS/cm.

Testing and Verification: Test pH, hardness, conductivity, TDS, alkalinity, sulfite, phosphate, and microbial counts.

System Monitoring: Adjust dosing and blowdown per readings; log all data.

### Shutdown Procedure

Notify Operations: Inform staff of planned shutdown.

Chemical Isolation: Stop chemical feed pumps and close valves; flush chemical lines.

System Drainage: Slowly open blowdown valves to release pressure and drain systems.

Rinse & Neutralize: Flush lines with clean water until neutral; use lay-up solution (200 ppm sodium sulfite) if idle long-term.

Recordkeeping: Log final readings, maintenance needs, and tag as 'Out of Service'.

## Sanitation and Maintenance

| Task | Frequency | Procedure |
| --- | --- | --- |
| Inspect softeners, filters, and tanks | Weekly | Check for leaks, salt bridging, pressure drop. |
| Clean strainers and filters | Bi-weekly | Flush and replace if fouled. |
| Test hardness, conductivity, pH, alkalinity | Daily | Compare with baseline and adjust feed. |
| Inspect RO membranes | Monthly | Flush with permeate; replace if DP >10 psi. |
| Biocide dosing / tower cleaning | Weekly / Monthly | Alternate oxidizing and non-oxidizing biocides. |
| Chemical inventory check | Weekly | Ensure proper labeling and SDS compliance. |
| Blowdown line inspection | Quarterly | Verify neutralization path and integrity. |
| Sensor calibration | Monthly | Verify pH, ORP, conductivity, and temperature accuracy. |

## Compliance Agencies / Code References

OSHA – 29 CFR 1910 – General Industry Standards (Chemical Handling, PPE, Lockout/Tagout)

EPA – Clean Water Act; NPDES Permitting for Discharge

ASME – Section VI & VII – Recommended Rules for Boiler Care and Operation

FDA / GMP – 21 CFR Part 210–211 for Water Purity (Pharma facilities)

AWWA – Water Quality and Disinfection Standards

ASHRAE – Guideline 12-2020: Legionellosis Risk Management

CDC – Legionella Water Management Program Guidelines

NJDEP / Local Codes – Compliance with State Discharge and Storage Regulations

## Safety Notes

• Wear gloves, face shield, and apron when handling chemicals.
• Never mix acids and caustics.
• Store incompatible chemicals separately.
• Ensure neutralization tanks are functional before blowdown.
• Maintain an accessible SDS binder near treatment systems.